ModbusControl

User manual

Table of contents

1	Install	2

2	Starting ModbusControl	2

3	The mbc project file	2

4	Using ModbusControl	2

4.1	Load/edit/save mbc project files	2

4.2	Import and export CSV files	3

4.3	Connect/disconnect/start polling/stop polling	3

4.4	Find/Filter	4

4.5	Diagnostics counters	4

4.6	Logging	4

4.7	Project configuration	4

4.8	Options	6

4.9	Commands menu	7

4.10	Help menu	8

4.11	The tab pages	8

4.12	Bit fields	8

4.13	Write a register	9

4.14	The status bar	9

5	Mbc project file validation with XSD schema	9

6	Logging	10

7	Modbus/TCP bridge	10

8	The Modbus protocol, function codes and word order	10

9	ModbusControl command line parameters	11

10	ModbusExport tool	12

11	ModbusImport tool	14

12	The Import/Export format	15

13	More about Modbus	16

14	Editing the mbc project file	16

14.1	Editing the XML	16

14.2	The <modbuscontrol> root element	16

14.3	The <size> element	17

14.4	The <modbus> element	17

14.5	The <tab> element	19

14.6	The <include> element	20

14.7	The <var> element	20

14.8	The <text> element	21

14.9	The <longdescr> element	22

14.10	The <type> element	22

14.11	The <enum> element	23

14.12	The <field> element	23

14.13	The <fcol> and <bcol> elements	24

14.14	The <autostart> element	25

14.15	The <modbustcpserver> element	25

14.16	XML comments	26

# Install

The installer installs the required program files in the “Program files\ED&A\ModbusControl” directory, together with an example mbc project file “Demo.mbc” and a user manual pdf.

The installer makes a Windows file association for the “.mbc” file extension. So when you double-click an mbc project file the ModbusControl application will be started automatically with that file.

ModbusControl requires the Microsoft .NET Framework 4.7.2 or higher.

# Starting ModbusControl

ModbusControl is usually started by double-clicking an mbc project file. ModbusControl automatically loads that project file, opens the connection and starts the communication.

You can also start ModbusControl from the Windows start menu, and use “File open” or “Recent project files” to open an mbc project file, press the “Open connection” button, and press the “Start polling” button.

Or start ModbusControl with command line parameters if you want to override the connection settings of the mbc project. See [ModbusControl command line parameters] for more information.

# The mbc project file

The mbc project file is an XML file that defines:

- TCP or serial connection parameters, slave ID, timeouts, sample rate and more.

- Tab pages with modbus register definitions.

- Modbus/TCP bridge server configuration.

- Preferred window size

# Using ModbusControl

## Load/edit/save mbc project files

The “File” menu has commands to open, reload and edit mbc project files.  
You can also drag and drop an mbc project file on the ModbusControl tab pages area.

Use the “Edit project file” menu item for editing the current mbc project file. ModbusControl then starts the editor that is associated with opening .txt files in Windows.
Editing the modbus registers directly in ModbusControl is not supported.

### The “Save project file…” menu item allows to update the mbc project file with the current connection and protocol settings, the current Modbus/TCP bridge settings, and the current form size. The next window lets you make a selection.

### The “Save project file…” menu item also has the “Update XML to current version” feature. This will update the mbc project file to the latest version, making all XML tags lower-case, and removing and/or replacing obsolete elements. It will also reformat the file.

The “Save project file” dialog will show a warning “Some connection parameters are overridden by the command line! If you save the current configuration to the mbc project file you may overwrite some parameters with the command line values!” if a command line override is in effect.

## Import and export CSV files

Export registers to file

Export reads the values of the registers from the modbus device and saves them in a CSV text file.

Select if you want to export the registers of the current tab page or the registers of all tab pages, select the export values format (int, uint, hex), and select the output file.

Press the “Start” button to start the export. The actual values of the registers will be read from the modbus device and saved into the CSV file. At the end of the export a summary line will show how many registers were exported and how many errors occurred. Registers that are defined as write-only are not exported since they can’t be read from the modbus device. The export will continue if modbus errors occur during the export. The errors will be reported in the log window.

The order is which the tab pages are exported to CSV can be controlled with the <exportorder> element. This is useful to have the registers in a certain order in the CSV file, with setup registers first for example, so that the import is done correctly.
See [The <tab> element] <exportorder> for more information on <exportorder>.

See [The Import/Export format] for more information on the CSV file format.

Import registers from file

Import reads register numbers and values from a CSV file and writes the values to the modbus device.

Press the “Select file” button to select the input file. Press the “Start” button to start the import. The file will be parsed first. If an error is found it will be reported in the log window and the import will not be started. Registers that are defined as read-only in the CSV file are not imported. The import will continue if modbus errors occur during the import. At the end of the import, a summary line will show how many registers were successfully written, how many registers were non-writeable and how many errors occurred.

See [The Import/Export format] for more information on the CSV file format.

Compare registers with file

Compare the actual values of the registers in the modbus device to the values in the CSV file.

Press the “Select file” button to select the input file. Press the “Start” button to start the compare. The file will be parsed first. If an error is found it will be reported and the compare will not be started. Registers that are defined as write-only in the CSV file are not compared since they can’t be read from the modbus device. Each register in the file will be compared to the register in the modbus device. The log window will show if the values were equal of different. You can choose to suppress the output for registers with equal value. The compare will continue if modbus errors occur during the compare. The errors will be reported in the log window. At the end of the compare a summary line will show how many registers had equal value, how many were different, how many were non-readable and how many errors occurred.

See [The Import/Export format] for more information on the CSV file format.

## Connect/disconnect/start polling/stop polling

Use the Connection menu (or speed buttons) to connect to a modbus device. Then the serial port is opened or a TCP connection is made.

Use the “Start polling”, “Stop polling” and “Poll once” commands to start/stop reading the modbus registers.

## Find/Filter

The “View” menu has a command to show a Find/Filter ribbon. This allows users to filter registers based on the register number or the register description text.

## Diagnostics counters

The “View” menu has a “Diagnostics counters” command that shows a window with a list of counters that show the number of reads, writes, errors, and a lot more.

## Logging

The “View” menu also has a “Logger” command that brings up the logger window. It can show all reads, writes, errors, warnings, and more. See [Logging] for more information.

## Project configuration

The “Project configuration” command in the “Extra” menu brings up the Project configuration window. Here, you configure the project’s parameters like connection type, baud rate, IP address, sample rate, endian settings, etc…

If a parameter is overridden by a command line option, then a warning icon is shown next to that parameter. Hoovering the mouse over the warning icon shows a warning text.

| Connection: |  | Serial/RTU: |  |  |  |  | A serial port connection using the modbus RTU protocol. |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Modbus/TCP: |  |  |  |  | A TCP network connection using the Modbus/TCP protocol. |
|  |  | RTU over TCP: |  |  |  |  | A TCP network connection using the serial RTU protocol. Useful when using serial-to-network bridges. |
| Serial interface: |  | Port: |  |  |  |  | Serial port name like COM1. |
|  |  | Baudrate: |  |  |  |  | Port speed in bits per second. 9600 and 19200 are common speeds. |
|  |  | Parity: |  |  |  |  | Parity setting. |
|  |  | EOM timeout: |  |  |  |  | End-of-message timeout: normally ModbusControl uses the “implied length” mechanism to detect the end of the response frames, but when the Modbus/TCP bridge is used and unknown function codes are used then this timeout is required to detect the end of the response frame. Default 100ms. |
|  |  | One-wire echo suppression: |  |  |  |  | To suppress the query command being echoed back to ModbusControl. This is only required if the serial port hardware causes ModbusControl to receive an echo of the command it sent. |
| TCP connection: |  |  | IP address: |  |  | IP v4 address like 192.168.1.52. Or 127.0.0.1 for local loopback for making the computer communicate with itself. |  |
|  |  |  | Port: |  |  | TCP port number. Modbus/TCP normally uses registered port 502. |  |
| Slave ID: | Slave ID number: 1 .. 255. Also called “slave address” or “unit identifier”. |  |  |  |  |  |  |
| Response timeout: |  |  |  | The maximum time ModbusControl waits for the first bytes of the response to arrive. In milliseconds. |  |  |  |
| Maximum frame size: |  |  |  | ModbusControl will construct its read queries so that the response will never be longer than this number of bytes. This allows to communicate with serial devices with small communication buffers. |  |  |  |
| Inter-frame delay: | Delay between receiving the last byte of a response and sending the next query. Modbus slaves on a serial multidrop network require this delay, as defined in the modbus specs. On serial port: “0 (auto)” means the default delay of 4 character lengths, like 4ms at 9600 baud. Values > 0 specify the delay in milliseconds. On TCP connection: an optional delay in milliseconds. Can also be used to reduce the load on the modbus device. |  |  |  |  |  |  |
| Functioncode to write holding registers: |  |  |  |  |  |  |  |
|  |  | Use FC6 only: |  |  |  |  | Use only function code 6 “write single register”. |
|  |  | Use FC16 only: |  |  |  |  | Use only function code 16 “write multiple registers”. |
|  |  | Auto select FC6 or FC16: |  |  |  |  | Automatically use FC6 for writing 16-bit registers and FC16 for writing multiple registers at once, like when writing 32-bit values. |
| 32-bit integer word order: how a 32-bit integer value is stored in 2 16-bit registers: |  |  |  |  |  |  |  |
|  |  | Low-High: |  |  |  |  | 32-bit registers are stored with the low bits in the first 16-bit register and the high bits in the second 16-bit register. |
|  |  | High-Low: |  |  |  |  | 32-bit registers are stored with the high bits in the first 16-bit register and the low bits in the second 16-bit register. |
| 32-bit float word order: how a 32-bit floating point value in the IEEE 754 format is stored in 2 16-bit registers: |  |  |  |  |  |  |  |
|  |  | Low-High: |  |  |  |  | The float value is stored with the low bits in the first 16-bit register and the high bits in the second 16-bit register. This mode is most used. |
|  |  | High-Low: |  |  |  |  | The float value is stored with the high bits in the first 16-bit register and the low bits in the second 16-bit register. |
| ASCII/string byte order: determines the order of characters in a word: |  |  |  |  |  |  |  |
|  |  | First char in low byte: |  |  |  |  | A register with value 0x4142 will be shown as “BA”. |
|  |  | First char in high byte: |  |  |  |  | A register with value 0x4142 will be shown as “AB”. This mode is most used. |
| Sample rate (ms): |  | The registers on the current tab page will be read from the modbus device periodically. The sample rate is the period in milliseconds. |  |  |  |  |  |
| Holding registers start: |  |  |  | Shows the holding registers numbering scheme. When start = 40001 or 400001: numbering schemes 40001-49999 and 400001-465536 can be used, simultaneously. When start = 40000 or 400000: numbering schemes 40000-49999 and 400000-465535 can be used, simultaneously. In numbering schemes 40001/40000, 9999 or 10000 registers can be accessed. In numbering schemes 400001/400000 all 65536 registers can be accessed. In the protocol, the first register is always referred to with address 0000. |  |  |  |
| Modbus/TCP bridge server: |  |  |  |  | Configuration of the built-in Modbus/TCP to modbus device bridge: See [Modbus/TCP bridge] for more information. |  |  |
|  |  | Enable: |  |  |  |  | Bridge enable/disable. |
|  |  | TCP port: |  |  |  |  | TCP port the bridge listens to, usually 502. |

## Options

Brings up the Options window with some general program settings:

| Beep on input error: | Enable/disable a beep sound when the user inputs an invalid value. |
| --- | --- |
| Move to next row on Enter: | When On: The cursor moves to the next line after entering a new value or pressing Enter in the grid. When Off: The cursor stays on the same line. Use Control-Enter to get the opposite action. |
| Auto-start edit mode on typing: | When On: The grid immediately switches to edit mode to enter a new value when the user starts typing characters in the grid. Normally, the user must double-click the value field or press the [F2] key to enter edit mode. |
| Show register properties column: | When On: shows an extra ‘Properties’ column in the grid that show the type (like int16), the r/w mode, decimals, etc… for each register. |
| Multiline rows with auto row size: | When On: allows registers with long description texts, or CR/LF’s in the text, to wrap around to the next line. When Off: all description text is shown in a single line and truncated if needed. |
| Clear Find/filter on tab change: | When On: the filter is cleared when the user switches to another tab page. When Off: the filter is active across tab pages. |
| Use XSD validation schema on project load: | When On: when an mbc project file is loaded it is validated against an XSD validation schema. See [Mbc project file validation with XSD schema] for more information. On by default. |
| Use custom editor: | Allows to configure the text editor used for editing mbc project files. By default ModbusControl uses the text editor that is associated with opening .txt files in Windows. Supports 1 parameter: %file: is replaced with the path to the file to be edited. Use double quotes around the path and around %file. For example, to use Windows notepad as editor, configure: "C:\windows\system32\notepad.exe" "%file" |
| Logger capacity: | Configures the maximum number of lines kept in memory by the logger. When the maximum is reached the oldest lines will be removed. |
| Stop polling on error: | Option to stop polling on read error. When polling is stopped because of an error, a message like this is shown: |
| Ignore form size on project reload: | When On: ModbusControl does not use the form size configured in the mbc project file when a project is reloaded. The form keeps its current size. Off by default. |
| Check for program updates: | Enable/disable the automatic check for updates each time the program is started. |

## Commands menu

### Send read

Command window to send a customized “read holding registers” query to the modbus device. You can setup the slave ID, first register number and number of registers to read.

Data can be shown in various formats.

### Send write

Command window to send a customized “write holding registers” query to the modbus device. You can setup the slave ID, first register number and number of registers to write. You also must provide the matching data.

Quantity always indicates the number of 16-bit registers to write.

Select function code 6 “write single register” or function code 16 “write multiple registers”. Select writing 16- or 32-bit registers. The write data format is automatically recognized and can be integer, unsigned integer, hexadecimal (with 0x prefix) or binary (with 0b prefix) format.

### Send custom command

Command window to send a custom modbus query. Enter the query in RTU protocol format, as hex bytes and space separated. First byte is slave ID, then function code, then data bytes. Do not include MBAP header or CRC because these are added automatically as needed.

For example: a function code 3 command to read the first 10 holding registers:

01 03 00 00 00 0A

Press the Send button to send the query. The response is also shown as a string of hex bytes.

## Help menu

To open the ModbusControl user manual.

To open a demo project file named Demo.mbc.

To check for a program update. The update check only works when connected to the ED&A network.

The about window shows the program version number and some extra info.

## The tab pages

The tab pages show the configured modbus registers, their description text and the value read. Or a possible error message.

Right-click the mouse on the Register or Description column to change the background color of the line. This allows to highlight the registers you are currently focusing on. 
Use the “Copy line” menu item to copy the whole line contents to the clipboard. Pressing Control-C after clicking the Register or Description column does the same.

Right-click the mouse on a register value to change the format in which the value is shown. You can choose:

- Int: show as signed integer

- UInt: show as unsigned integer

- Hex: show as hexadecimal numbered, like 0x1234

- Binary: show as binary value, like 0b10010110

- Float: show as a floating point value. Requires IEEE 754 format. Can only be used on 32-bit registers.

- ASCII: show as ASCII characters. A 16-bit register is shown as 2 ASCII characters, a 32-bit register as 4 ASCII characters. Non-printable ASCII codes are shown as escape sequences, for example a register with value 0x0141 is shown as “\x01A”.

The check mark shows the current format. 
Use the “Copy value” menu item to copy the value to the clipboard. Pressing Control-C after clicking the Value column does the same.

## Bit fields

Some registers may be defined having bit fields. These registers have a [+] icon in front. Clicking the [+] icon expands the register and shows the bit fields. Click the [-] icon to collapse the bit fields.

## Write a register

If a register or bitfield is writeable, its value can be edited by double-clicking the value field or by pressing the [F2] key on the selected line. If the “Auto-start edit mode on typing” option is on editing is automatically started when the user hits a character key.

You can enter the new value as a positive or negative decimal value, in hex format starting with “0x” (as 0x1234), in binary format starting with “0b” (as 0b1101) or in ASCII starting with double-quote. (as “AB”). The new value you enter will be checked if it is a valid value and if it fits in the width of the register or bit field. Press the [Escape] key if you want to abort the input.

When you change the value of a bit field ModbusControl will calculate a new value for the entire register, depending on the actual values of the other bit fields of the register.

If the value is displayed as an enum value, then a dropdown will show a list of values to choose from on edit:

If the “Move to next row on enter” option is on the row selection moves to the next row after entering the new value.

## The status bar

During normal operation the status bar shows the number of reads, the number of times ModbusControl did not receive a response and the number of times it received an invalid response. It also shows many informational messages for a few seconds.

The status bar turns blue when there is no connection or no polling.
The status bar turns red for error messages.

Hoover the mouse cursor above the status bar to see the last informational or error message again.

# Mbc project file validation with XSD schema

ModbusControl now uses an XML validator to validate the mbc project file. When an mbc project file is loaded is will first be validated against an XSD schema. If it does not pass validation you will get an error message but you can choose to ignore this for now and load the file anyway.

The schema validation only allows XML tags in lower-case. And it only allows the currently supported XML elements. Some XML elements that are obsolete are removed and/or replaced.

We also experienced that many mbc project files have errors that weren’t detected when loading a project file. That is because ModbusControl searches for the XML elements that it knows and ignores all others. With schema validation this is no longer allowed. Only currently supported XML elements are allowed.

If needed, the schema validation can be turned off in the Options menu.

ModbusControl can convert an old mbc project file to the new format. See [Load/edit/save mbc project files] for more.

Please make sure that all your mbc project files are modified to conform to the validation over time.

If you send an mbc project file to an external partner, make sure it conforms to the schema validation.

# Logging

ModbusControl has a built-in logging mechanism that can log:

- Errors, like response timeouts

- Warnings

- Information messages, like connection opened

- Trace TX/RX: the modbus messages sent to and received from the modbus device

- Read queries: the modbus read commands used to fetch the current values of the registers

- Write queries: the user changing the values of registers

- Bridge info: clients connecting to and disconnecting from the Modbus/TCP bridge

- Bridge data: the Modbus/TCP frames received and sent over the Modbus/TCP bridge

- Bridge decode: the Modbus/TCP frames received and sent over the bridge decoded to human-readable messages like “Slave=1, Read holding registers: addr=100, quant=15”

You can start and stop the logger, clear it, copy the log to the Windows clipboard (in CSV format) or save the log into a file in CSV format.

# Modbus/TCP bridge

ModbusControl has a built-in Modbus/TCP server that acts as a bridge to the connected modbus device. This allows Modbus/TCP clients like ModbusScope to communicate with the serial modbus device as well. It also allows multiple Modbus/TCP clients or more copies of ModbusControl to be connected to the modbus device simultaneously. Works for all connection types to the modbus device, not only the serial line.

A query received from a modbus client is buffered till the communications line to the modbus device becomes available. Then it is forwarded. As soon as the response is received it is sent back to the Modbus/TCP client that sent the query. When a response timeout is detected the appropriate exception message is sent back to the Modbus/TCP client.

The Modbus/TCP protocol query has a “unit identifier” byte. This byte is used as “slave ID” in the forwarded query to the modbus device. So it must match the “slave ID” of a connected modbus device to get a response. Some Modbus/TCP clients don’t care about the unit identifier and send 0x00 of 0xFF.

The speed of the serial line to the modbus device is limited. This puts a limit on the number of Modbus/TCP clients and their sample rates!

The Modbus/TCP bridge can be configured from the Options – Project Configuration menu.

# The Modbus protocol, function codes and word order

ModbusControl supports the Modbus RTU (binary) and Modbus/TCP protocols only! ASCII mode is not supported.

ModbusControl currently only supports reading and writing of “Holding Registers” using modbus function codes 03 (Read Holding Registers), 06 (Write Single Register) and 16 (Write multiple registers). Modbus Holding Registers are 16-bit registers.

32-bit registers are simply 2 consecutive 16-bit registers. 32-bit integer values are transferred in low-high word order or high-low word order. ED&A prefers low-high word order. This is selected in the project configuration with “32-bit integer word order” or in the mbc project file with the <int32endian> element.

Floating point values are also supported, in 32-bit single precision IEEE 754 format. These too require 2 consecutive 16-bit registers and can be transferred in low-high word order or high-low word order. ED&A prefers low-high word order. This is selected in the project configuration with “32-bit float word order” or in the mbc project file with the <float32endian> element.

In a Modbus command message, registers are addressed starting at zero. The first holding register is referred to as address 0 in the query message. For historic reasons 16-bit holding registers are often referred to as registers 40001..49999. The base for the register numbering is defined in the mbc project file with the <holdingregisterstart> element. It usually is 40001 or 400001. But 40000 and 400000 are also allowed. It is usually chosen to match the documentation of the modbus device.

ModbusControl always tries to read as many consecutive registers as possible with a single “Read Holding Registers” query to improve performance. The number of registers read with a single query is limited by the “Maximum frame size” parameter. ModbusControl generates the queries so that the responses from the device will not be longer than this.

If ModbusControl receives an “illegal data address” exception on a “Read Holding Registers” query, it may be that it tries to read more registers than the device supports. To show the values of the existing registers and to show which registers don’t exist it re-reads these registers one by one.

To write holding registers ModbusControl uses either function code 06 “Write Single Register” or 16 “Write Multiple Registers”. See [Functioncode to write holding registers] in [Project configuration] for more information.

# ModbusControl command line parameters

Command line options allow to override the connection parameters.

Example usage:

Modbuscontrol Test1.mbc -connection serialrtu -port COM6 -baudrate 19200

Modbuscontrol Test1.mbc -connection modbustcp -ipaddress 192.168.1.123

Mbc filename is optional.

Use - or / for options:

| -connection <type> | Connection type: ‘serialrtu’, ‘modbustcp’ or ‘rtutcp’. Default: serialrtu |
| --- | --- |
| -port <name> | Serial port name: COM1,… Default: COM1 |
| -baudrate ### | Serial port baudrate. Default: 9600 |
| -parity <mode> | Serial port parity: ‘odd’, ‘even’, ‘none’, ‘mark’ or ‘space’. Default: None |
| -endofmessagetimeout ### | Serial port end-of-message timeout (ms). Default: 100ms |
| -onewire | 1-wire operation, ignore query/command echo. Default: off |
| -ipaddress <address> | Slave/server IP address, like 192.168.1.100. Default: <none> |
| -ipport ### | Slave/server IP port, usually 502. Default: 502 |
| -slaveid ### | Slave ID number: 1 – 255. Default: 1 |
| -maxframe ### | Maximum frame size: 13 – 256 bytes. Default: 256 |
| -responsetimeout ### | Maximum wait time for first byte of response (ms). Default: 1000ms |
| -interframedelay ### | Delay before sending next query (ms). Default: 0 (auto) |
| -writeregfc <mode> | Write holding registers function code: ‘6’, ‘16’ or ‘auto’. Default: auto |
| -samplerate ### | Set the polling period for reading the registers from the slave/server (ms). Default:1000ms |
| -? or -h or -help | Show the command line help screen |

The command line parameters are used only when the program is started. They are ignored when the mbc project file is reloaded or another one is loaded.

# ModbusExport tool

ModbusExport.exe is a command line tool to export registers from a modbus device to a CSV file.
It exports all readable registers of all tabs of an mbc file, and their current values, to a CSV file.

See [The Import/Export format] for more information on the CSV file format.

Example usage:

ModbusExport Test1.mbc Data1.csv

ModbusExport Test1.mbc Data1.csv -connection modbustcp -ipaddress 192.168.1.100 
    -format int -log log1.txt

ModbusExport Test1.mbc Data1.csv -tabs ‘Base setup” “Setup” “Parameters”

Mbc filename (or path) is required.

CSV filename (or path) is required.

Use - or / for options:

| -connection <type> | Connection type: ‘serialrtu’, ‘modbustcp’ or ‘rtutcp’. Default: serialrtu |
| --- | --- |
| -port <name> | Serial port name: COM1,… Default: COM1 |
| -baudrate ### | Serial port baudrate. Default: 9600 |
| -parity <mode> | Serial port parity: ‘odd’, ‘even’, ‘none’, ‘mark’ or ‘space’. Default: None |
| -endofmessagetimeout ### | Serial port end-of-message timeout (ms). Default: 100ms |
| -onewire | 1-wire operation, ignore query/command echo. Default: off |
| -ipaddress <address> | Slave/server IP address, like 192.168.1.100. Default: <none> |
| -ipport ### | Slave/server IP port, usually 502. Default: 502 |
| -slaveid ### | Slave ID number: 1 – 255. Default: 1 |
| -maxframe ### | Maximum frame size: 13 – 256 bytes. Default: 256 |
| -responsetimeout ### | Maximum wait time for first byte of response (ms). Default: 1000 |
| -interframedelay ### | Delay before sending next query (ms). Default: 0 (auto) |
| -int32endian <endian> | 32-bit int word order: ‘little’ or ‘big’. Default: Little |
| -float32endian <endian> | 32-bit float word order: ‘little’ or ‘big’. Default: Little |
| -stringendian <endian> | String byte order: ‘little’ or ‘big’. Default: Big |
| -format <format> | Export format: ‘default’, ‘int’, ‘uint’ of ‘hex’. Default: ‘default’: format as given in mbc file. |
| -stringformat <format> | String export format: ‘ascii’, ‘int’, ‘uint’ or ‘hex’. Default: ascii |
| -tabs <tabname> [tabname]... | Names of tab pages to export, in this order, case insensitive, tab names can be quoted. No default. |
| -log <file/path> | Append output to a log file. Default: no logging |
| -logtime | Add timestamps to the log file. |
| -cont | Continue on error if reading of single register fails. Default: off |
| -verbose | Displays verbose output. Default: off |
| -? or -h or -help | Shows the command line help screen. |

Exit codes: 	0 = No error
 		1 = Command line error
 		2 = File error
 		3 = Communication error

# ModbusImport tool

ModbusImport.exe is a command line tool to import registers from a CSV file into a modbus device.
It writes all writeable registers that are in the file to the device.

See [The Import/Export format] for more information on the CSV file format.

Example usage:

ModbusImport Test1.mbc Data1.csv

ModbusImport Data1.csv -connection modbustcp -ipaddress 192.168.1.100

ModbusImport Data1.csv -connection modbustcp -ipaddress 192.168.1.100 -tabs Setup

Mbc filename is optional. If given, the connection parameters (like connection type, IP address, serial port, baudrate, …) are taken from the mbc file. These can be overridden by command line options. If no mbc file is given all necessary connection parameters (like connection type, IP address, serial port, baudrate, …) must be specified by command line options.

CSV filename (or path) is required.

Use - or / for options:

| -connection <type> | Connection type: ‘serialrtu’, ‘modbustcp’ or ‘rtutcp’. Default: serialrtu |
| --- | --- |
| -port <name> | Serial port name: COM1,… Default: COM1 |
| -baudrate ### | Serial port baudrate. Default: 9600 |
| -parity <mode> | Serial port parity: ‘odd’, ‘even’, ‘none’, ‘mark’ or ‘space’. Default: None |
| -endofmessagetimeout ### | Serial port end-of-message timeout (ms). Default: 100ms |
| -onewire | 1-wire operation, ignore query/command echo. Default: off |
| -ipaddress <address> | Slave/server IP address, like 192.168.1.100. Default: <none> |
| -ipport ### | Slave/server IP port, usually 502. Default: 502 |
| -slaveid ### | Slave ID number: 1 – 255. Default: 1 |
| -maxframe ### | Maximum frame size: 13 – 256 bytes. Default: 256 |
| -responsetimeout ### | Maximum wait time for first byte of response (ms). Default: 1000 |
| -writeregfc <mode> | Write holding registers function code: ‘6’, ‘16’ or ‘auto’. Default: auto |
| -interframedelay ### | Delay before sending next query (ms). Default: 0 (auto) |
| -int32endian ### | 32-bit int word order: ‘little’ or ‘big’. Default: Little |
| -float32endian ### | 32-bit float word order: ‘little’ or ‘big’. Default: Little |
| -stringendian ### | String byte order: ‘little’ or ‘big’. Default: Big |
| -tabs <tabname> [tabname]... | Names of tab pages to export, in this order, case insensitive, tab names can be quoted. No default. |
| -log <file/path> | Append output to a log file. Default: no logging |
| -logtime | Add timestamps to the log file. |
| -cont | Continue on error if writing of register fails. Default: off |
| -verbose | Displays verbose output. Default: off |
| -? or -h or -help | Shows the command line help screen. |

Exit codes: 	0 = No error
 		1 = Command line error
 		2 = File error
 		3 = Communication error

# The Import/Export format

ModbusControl can export register values to a CSV file and import register values from a CSV file. A CSV file is a human-readable text file with 1 line per register and the fields of a register are separated by semicolons. The file type is .CSV by default. CSV files can be opened in MS Excel.

The ModbusControl CSV file uses a semicolon (;) as field separator. This is European style and compatible with Windows regional settings and MS Excel in Europe.

Lines starting with # are comment lines. Comment lines are ignored on import and compare.

A field containing the separator, carriage return or linefeed must be quoted with the double quote character ("). A field containing the double quote character (") itself will be quoted and each quote in the field must be escaped with a preceding quote (doubled). Like "My name is ""John""". This is compatible with MS Excel.

On export the Windows system default encoding will be used. Which is usually ANSI codepage 1252 in Western Europe. This allows easy import in Excel because Excel uses the Windows default encoding too for import and export.

The import ignores empty lines, lines with only spaces and lines with only.

Example import/export line:

40108;16;"Analog in V1 (0-1000)";r;UInt;861
│      │  │                        │  │    │
│      │  │                        │  │    Value (can be signed, unsigned, hex, float, ASCII)
│      │  │                        │  Format (Int, UInt, Hex, Binary, Float, ASCII)
│      │  │                        “r” and/or “w” for read/write
│      │  Register description text
│      Register size, 16 or 32 bits
Register number, usually 40001-49999 for modbus holding registers

Import files can have 2, 3, 4 ,5 or 6 fields. They are used as this:

| 2 fields | Register (16-bit), Value (16-bit) |
| --- | --- |
| 3 fields | Register, Size (16/32), Value |
| 4 fields | Register, Size (16/32), Description, Value |
| 5 fields | Register, Size (16/32), Description, RW, Value |
| 6 fields | Register, Size (16/32), Description, RW, Format, Value |

# More about Modbus

For more information on the modbus protocol, visit www.modbus.org. Look for:

- Technical Resources

- Modbus Specifications

- MODBUS Protocol Specification

- Modbus Serial Line Protocol and Implementation Guide

# Editing the mbc project file

## Editing the XML

The mbc project file is an XML formatted text file that is both human-readable and machine-readable. ModbusControl does not (yet) support creation of a project file so it has to be edited manually. You can also use the example project Demo.mbc to start from. You’ll find it in the Help menu.

Some editors like Notepad++ recognize an XML file and apply XML syntax coloring. This makes the editing easier.

XML tags are case sensitive! Nowadays ModbusControl uses all lowercase XML tags, but older versions used a mix of camel-case tags like “SampleRate” and lowercase tags. It is recommended to use all lowercase tags now. ModbusControl still recognizes the old camel-case tags for compatibility.

## The <modbuscontrol> root element

An XML file requires a single <modbuscontrol> root element that contains all the other elements. It supports the following elements:

| <size> | Defines the size of the ModbusControl window. |
| --- | --- |
| <modbus> | Configures communication parameters to the modbus device. |
| <modbustcpserver> | Configures the built-in Modus/TCP bridge. |
| <autostart> | Configures the auto-start option. |
| <tab> | Configures one or more tab pages with modbus registers. |
| <include> | Allows one mbc file to include the tab pages of another mbc file. |

## The <size> element

The <size> element defines the size of the ModbusControl window when opening the project. Is optional. Can contain the following elements:

| <width> | The program window’s default width. |
| --- | --- |
| <height> | The program window’s default height. |

For a 96-DPI system these values represent the window size in pixels. On high-DPI systems these values are scaled to result in a window that looks the same size as on 96-DPI systems.

Example:

<size>
	<width>580</width>
	<height>600</height>
</size>

## The <modbus> element

The <modbus> element defines the connection to the modbus device. All elements are optional.
See [Project configuration] for more details. 
Can contain the following elements:

| <connection> | Type of connection and protocol used. Value “serial/rtu” for serial port with RTU protocol. Value “modbus/tcp” for TCP connection with Modbus/TCP protocol. Value “rtu/tcp” for TCP connection with RTU protocol. |
| --- | --- |
| <port> | Serial port name, like “COM1”. |
| <baudrate> | Serial port speed in bits per second. 9600 and 19200 are common speeds. |
| <parity> | Serial port parity setting, like “None”, “Even” or “Odd”. |
| <endofmessagetimeout> | Serial port end-of-message timeout: normally ModbusControl uses the “implied length” mechanism to detect the end of the response frames, but when the Modbus/TCP bridge is used and unknown function codes are used then this timeout is required to detect the end of the response frame. Time in milliseconds. Default 100ms. |
| <onewireechosuppression> | One-wire echo suppression: To suppress the query command being echoed back to ModbusControl. Value “true” or “false”. |
| <ipaddress> | IP v4 address like “192.168.1.52”. Or “127.0.0.1” for local loopback for making the computer communicate with itself. |
| <ipport> | TCP port number. Modbus/TCP normally uses registered port 502. |
| <slaveid> | Slave ID number: 1 .. 255. Also called “slave address” or “unit identifier”. |
| <responsetimeout> | The maximum time ModbusControl waits for the first bytes of the response to arrive. In milliseconds. |
| <maximumframesize> | Maximum frame size: ModbusControl will construct its read queries so that the response will never be longer than this number of bytes. This allows to communicate with serial slaves with small communication buffers. |
| <interframedelay> | Inter-frame delay: Delay between receiving the last byte of a response and sending the next query. Modbus slaves on a serial multidrop network require this delay, as defined in the modbus specs. On serial port: 0 means the default delay of 4 character lengths, for example 4ms at 9600 baud. Values > 0 are delay in milliseconds. On TCP connection: 0 is no delay. Values > 0 are delay in milliseconds. Can also be used to reduce the load on the Modbus slave or server. |
| <writeholdingregisterfc> | Value “6” or “06”: Use only function code 6 “write single register”. Value “16”: Use only function code 16 “write multiple registers”. Value “auto”: Automatically use FC6 for writing 16-bit registers and FC16 for writing multiple registers at once, like when writing 32-bit registers. |
| <int32endian> | Defines how a 32-bit integer value is stored in 2 16-bit registers. Value “little” for low-high word order: the low bits in the first 16-bit register and the high bits in the second 16-bit register. Value “big” for high-low word order: the high bits in the first 16-bit register and the low bits in the second 16-bit register. Note: older versions supported the <Value32BitEndian> element but that has been replaced with <int32endian> and <float32endian>. <Value32BitEndian> is now automatically replaced by <int32endian>. |
| <float32endian> | Defines how a 32-bit floating point value is stored in 2 16-bit registers. Value “little” for low-high word order: the low bits in the first 16-bit register and the high bits in the second 16-bit register. Value “big” for high-low word order: the high bits in the first 16-bit register and the low bits in the second 16-bit register. |
| <ascii16endian> | Defines the order of characters in a word: Value “little” for first char in low byte. Value “big” for first char in high byte. |
| <samplerate> | The registers on the current tab page will be read from the modbus device periodically. This defines the period in milliseconds. |
| <holdingregisterstart> | Defines the holding registers numbering scheme. This is the number of the first holding register. Value 40001 or 400001: numbering schemes 40001-49999 and 400001-465536 can be used, simultaneously. Value 400000 or 400000: numbering schemes 40000-49999 and 400000-465535 can be used, simultaneously. In numbering schemes 40001/40000, 9999 or 10000 registers can be accessed. In numbering schemes 400001/400000 all 65536 registers can be accessed. In the protocol, the first register is always referred to with address 0000. |

Example:

<modbus>

<connection>serial/rtu</connection>

<port>COM1</port>

<baudrate>19200</baudrate>

<parity>none</parity>

<endofmessagetimeout>100</endofmessagetimeout>

<slaveid>1</slaveid>

<responsetimeout>1000</responsetimeout>

<maximumframesize>256</maximumframesize>

<writeholdingregisterfc>16</writeholdingregisterfc>

<int32endian>little</int32endian>

<float32endian>little</float32endian>

<ascii16endian>little</ascii16endian>

<samplerate>1000</samplerate>

</modbus>

## The <tab> element

Each tab element defines a tab page for the user. Each tab page has a name and a list of variables. A variable is a modbus register with description text, numeric type and format.
Can contain the following elements:

| <name> | The name of the tab page, like “Temperatures”. |
| --- | --- |
| <exportorder> | The order is which the tab pages are exported to CSV. This is useful to have the registers in a certain order in the CSV file, with setup registers first for example, so that the import is done correctly. Use positive integer numbers like 0, 1, 2, 3, or 100, 200, 300, up to 4294967295. The tab pages are exported in order of ascending exportorder number. Tab pages that do not have an exportorder number are exported lastly, and in order of appearance in the mbc file. Optional. |
| <fcol> | Sets the default font (text) color for all <var> on this tab page. See [The <fcol> and <bcol> elements] for details. Optional. |
| <bcol> | Sets the default background color for all <var> on this tab page. See [The <fcol> and <bcol> elements] for details. Optional. |
| <expandfields> | Allows to have the bit fields of all <var> on this tab page to be already expanded when the project is loaded. Valid values are “true” and “false”. Optional. Default is false. |
| <var> | One or more definitions of modbus registers that are displayed on this tab page. Each with register number, size, description text, size, numeric type and format, etc... |

Example of a <tab> element:

<tab>
<name>Inputs (read only)</name>
<var><reg>40001</reg><text>Software version Major</text><type>int16</type> 
  <rw>r</rw></var>
<var><reg>40002</reg><text>Software version Minor</text><type>int16</type> 
  <rw>r</rw></var>
</tab>

## The <include> element

The <include> element includes the tab pages and registers of another mbc file. Other elements like <size> and <modbus> are ignored.

This is intended to have a set of tab pages with special registers to de defined in another mbc project file. The <include> normally reports an error if the specified file is not found, but this can be disabled. An mbc file can have multiple <include> statements, and each of those mbc files can in turn have <include> statements.

Can contain the following elements:

| <file> | The name of (or path to) the mbc file to be included. |
| --- | --- |
| <required> | When true: an error is reported if the mbc file is not found. When false: no error is reported if the mbc file is not found. Default is true. |

Examples of <include> elements:

<include>

<file>Configuration.mbc</file>

<required>false</required>

</include>

<includex>

<file>C:\Projects\Special\Calibration.mbc</file>

</include>

## The <var> element

Each <var> defines 1 variable (or modbus register) that is displayed as 1 row in the grid.
Can contain the following elements:

| <reg> | The modbus register number. Numbering depends on the <holdingregisterstart> element. Holding registers numbering usually starts at 40001. |
| --- | --- |
| <text> | The text that describes the register. See [The <text> element] for details. |
| <longdescr> | A possibly long descriptive text that is shown as a tooltip when the user hovers the mouse over the text description. Can be multi-line by using CR/LF’s. |
| <type> | The type of the register. This defines the size of the register (16 or 32-bit) and if it is displayed as signed or unsigned decimal, hexadecimal, etc. See [The <type> element] for details. |
| <minlen> | Determines the minimum number of digits shown for the value. It adds leading zeros if needed. It is useful when showing a register value in binary or hexadecimal format to avoid that the value jumps left and right when the upper bits change. Example: 15 (decimal) with hex format and minlen=4 will be shown as “0x000F”. Optional. Default is 0. |
| <rw> | Determines if the register if read only, write only or read/write. Can be “r”, “w” or “rw”. ModbusControl will only attempt to read registers that have the “r” property, and it will only allow writing of registers that have the “w” property. Optional. Default is “r”. |
| <fcol> | Sets the font (text) color of the register, description and value. See [The <fcol> and <bcol> elements] for details. Optional. |
| <bcol> | Sets the background color of the register, description and value. See [The <fcol> and <bcol> elements] for details. Optional. |
| <decimals> | If > 0 the value is shown with this number of decimals. For example a value of 12345 with dec=2 is shown as 123,45. Allowed only for Int and UInt types. Optional. Default is 0. Valid values are 0 to 12. |
| <enum> | Enumeration defines a list of texts that match specific values, like a set of named constants. ModbusControl shows the matching enum text after the numeric value in the value column. See [The <enum> element] for more information. Optional. |
| <field> | Allows to define one or more bit fields in the register. If a register has bit fields it can be expanded to view the value of each bit field separately. This makes it easy for example to inspect the status of digital inputs that are packed as a bitmap in a register. See [The <field> element] for more information. Optional. |
| <expandfields> | Allows to have this register’s bit fields already expanded when the project is loaded. Valid values are “true” and “false”. Optional. Default is false. |

Example of a simple <var> element:

<var><reg>40001</reg><text>Counter 1</text><type>int16</type>
 <rw>rw</rw></var>

Example of a <var> element with one decimal and a light red background:

<var><reg>40025</reg><text>Temperature 1 (0,1 deg)</text><type>int16</type>
 <decimals>1</decimals><rw>r</rw><bcol>255,200,200</bcol>
 </var>

## The <text> element

The description text that is shown with the register. XML provides escape sequences for using characters which are problematic to include directly.

There are five predefined entities:

| &lt; | represents < |
| --- | --- |
| &gt; | represents > |
| &amp; | represents & |
| &apos; | represents ‘ |
| &quot; | represents " |

Other special characters must be written with a numeric character reference. All permitted Unicode characters may be represented with a numeric character reference. For example:

<text>Temperature 1 (&#176;C)</text>    shows “Temperature 1 (°C)”

There is an extensive list of Unicode code points used in XML/HTML on:

http://en.wikipedia.org/wiki/List_of_XML_and_HTML_character_entity_references

http://nl.wikipedia.org/wiki/Lijst_van_HTML-entiteiten.

## The <longdescr> element

The <longdescr> element sets an extra description text that is shown as a tooltip. A tooltip is often used to specify extra information about something when the user hoovers the mouse pointer over an element.

| <longdescr> | Set the tooltip text for this register. Can be multi-line by using CR/LF characters in the text. Also, a CR/LF can be written as an XML escape sequence with &#13; |
| --- | --- |

For example:

<var>

<reg>40004</reg>

<text>Digital inputs (bitmap)</text>

<longdescr>Digital inputs bitmap. &#13;Each bit in this register corresponds to the on/off state of a digital input.</longdescr>

<type>bin16</type>

## The <type> element

The <type> element defines the type of the register. This defines the size of the register as 16 or 32-bit, and the display format like signed, unsigned, hexadecimal, etc...

Supported types:

| int16 | Signed integer, 16-bit. |
| --- | --- |
| uint16 | Unsigned integer, 16-bit. |
| int32 | Signed integer, 32-bit. Uses two 16-bit registers. |
| uint32 | Unsigned integer, 32-bit. Uses two 16-bit registers. |
| hex16 | Hexadecimal representation, 16-bit. 1000 (decimal) will be shown as 0x3E8. |
| hex32 | Hexadecimal representation, 32-bit. Uses two 16-bit registers. |
| bin16 | Binary representation, 16-bit. 1000 (decimal) will be shown as 0b1111101000. |
| bin32 | Binary representation, 32-bit. Uses two 16-bit registers; |
| float32 | Floating point value. Must be encoded in 32-bit IEEE-754 format. Uses two 16-bit registers. |
| ascii16 | 2 ASCII characters, For example a register with value 16706 or 0x4142 will be shown as “AB”. Order is defined by configuration. |
| ascii32 | 4 ASCII characters, For example a register with value 1128546626 or 0x43444142 will be shown as “ABCD”. Order is defined by configuration. |

## The <enum> element

The enum element sets a list of texts which match certain values, like a set of named constants. ModbusControl shows the matching enum text after the numeric value in the value column.

The <enum> element contains a number of <item> elements. Each <item> element specifies a  value and the corresponding text.

For example, this enum defines enum texts for the values 0, 1, 2, 3 and 4.

<enum>

<item><value>0</value><text>no alarm</text></item>

<item><value>1</value><text>T1 FAIL</text></item>

<item><value>2</value><text>T1 TOO HOT</text></item>

<item><value>3</value><text>T2 FAIL</text></item>

<item><value>4</value><text>T2 TOO HOT</text></item>

<else>UNRECOGNIZED VALUE!</else>

</enum>

Each value can appear only once in an enum. 
The <else> element is optional.

If the value of the register does not match any of the values specified in the enum, and there is an <else> element, the text of the <else> element will be shown. 
If there is no <else> element, then “(enum ?)” will be shown.
The <else> element can be left empty to suppress the  message.

## The <field> element

Each field element defines a bit field in the register. A bit field can have a width of 1 bit or more. If a register has bit fields it can be expanded to view the value of each bit field.

The <field> element can contain the following elements:

| <pos> | The number of the lowest bit of this bit field. 0 for the lowest bit of the register. |
| --- | --- |
| <width> | Determines the number of bits of the bit field. Optional. Default is 1. |
| <text> | The text that describes the bit field. See [The <text> element] for details. |
| <longdescr> | A possibly long descriptive text that is shown as a tooltip when the user hovers the mouse over the text description. Can be multi-line by using CR/LF’s. |
| <type> | The type of the bit field. This defines if it is displayed as signed or unsigned decimal, hexadecimal, etc... Can be “int”, “uint”, “hex”, “bin” or “ascii”. Optional. Default is “uint”. |
| <minlen> | Determines the minimum number of digits shown for the value. It adds leading zeros if needed. Optional. Default is 0. |
| <fcol> | Sets the font (text) color of the bit field, description and value. See [The <fcol> and <bcol> elements] for details. Optional. |
| <bcol> | Sets the background color of the bit field, description and value. See [The <fcol> and <bcol> elements] for details. Optional. |

Example of a <field> element, defines 1 bit:

<field><pos>0</pos><text>RESET button</text></field>

Example of a <field> element with width 4, on bits 11..8, shown in hex:

<field><pos>8</pos><width>4</width><text>Mode</text><type>hex</type></field>

Example of a <var> element with bit fields:

<var><reg>40009</reg><text>Digital inputs (bitmap)</text>
 <type>bin16</type><minlen>8</minlen><rw>r</rw>
 <field><pos>0</pos><text>RESET button</text></field>
 <field><pos>1</pos><text>IN1</text></field>
 <field><pos>2</pos><text>IN2</text></field>
 <field><pos>3</pos><text>IN3</text></field>
</var>

## The <fcol> and <bcol> elements

The <fcol> and <bcol> elements define the font (text) and background colors. A color can be specified in 3 ways:

- With 3 RGB values 0 – 255 defining the red, the green and the blue component. 
For example:

| <bcol>255,0,0</bcol> | Shows a bright red background. |
| --- | --- |
| <bcol>0,255,0</bcol> | Shows a bright green background. |
| <bcol>255,255,180</bcol> | Shows a soft yellow background. |

- As a HTML color specification, as #RRGGBB. Where RR, GG and BB are 2 hexadecimal digits each, with range 00 .. FF. 
For example:

| <bcol>#FF0000</bcol> | Shows a bright red background. |
| --- | --- |
| <bcol>#00FF00</bcol> | Shows a bright green background. |
| <bcol>#FFFFB4</bcol> | Shows a soft yellow background. |

- By color name. Like Red, Green, Aqua, Gold, Royalblue, Steelblue, Mediumblue, Darkblue, Royalblue, Deepskyblue, etc…

| <bcol>royalblue</bcol> | Shows a “royal blue” background. |
| --- | --- |

Here’s a chart showing all colors with their names and RGB values. Zoom in to read the names :-)

## The <autostart> element

The <autostart> element defines if the communication is started automatically when the project is opened, and optionally which tab page is shown.

When there is no <autostart> element the communication is started automatically and the first tab page is shown. This is for compatibility with older versions. When an <autostart> element is defined then autostart is determined by the <enable> element.

| <enable> | Enables or disables the autostart. Valid values are “true” and “false”. Optional. Default is false. |
| --- | --- |
| <page> | Defines which tab page is shown on autostart. This can be the name of the tab page like “Inputs”, or the tab page number starting from 1. Optional. Default is the first tab page. |

## The <modbustcpserver> element

The <modbustcpserver> element configures the built-in Modbus/TCP server that acts as a bridge to the connected modbus device. This allows other Modbus/TCP clients to be connected to the serial modbus device simultaneously.

See [Modbus/TCP bridge] for more information.

| <enable> | Enables or disables the bridge. Valid values are “true” and “false”. Optional. Default is false. |
| --- | --- |
| <port> | The TCP port the bridge listens to. Optional. Default is 502. |

## XML comments

To hide parts of the tabs or registers temporarily, you can mark them as XML comments. Then ModbusControl will ignore them.

XML comments start with

<!--

and end with

-->

Example where 2 var lines are “commented out”:

<var><reg>40006</reg><text>Analog in 1</text><type>uint16</type><rw>r</rw></var>

<!--

<var><reg>40007</reg><text>Analog in 2</text><type>uint16</type><rw>r</rw></var>

<var><reg>40008</reg><text>Analog in 3</text><type>uint16</type><rw>r</rw></var>

-->

<var><reg>40009</reg><text>Analog in 4</text><type>uint16</type><rw>r</rw></var>